## Table 1
HD8000 Technical Speciﬁcations
HD8000- |  |  |  | 3306 | 3308 |  | 3310 | 3312 |  | 2624 | AA30 | 6640 |  | AA60
Basical Rectiﬁcation | Input voltage |  |  | 3300V | [5 empty] | 1900V | 10kV | 6600V |  | 10kV
| Input frquency |  |  | 45Hz-66Hz
| Overload |  |  | 110%@ rated current, 120%@ rated current 60s
| Eﬃciency |  |  | ≥99%
| Power factor |  |  | ≥0.95 (Rated current, equipped with 2% AC input reactor)
| Protection |  |  | overload protection, overheat protection, short circuit protection, fault pre-judgment, etc
PWM Rectiﬁcation | Input frquency |  |  | 45Hz-66Hz
| Overload |  |  | 110%@ rated current, 120%@ rated current 60s
| Eﬃciency |  |  | ≥98.5%
| Power factor |  |  | adjustable (default 1)
| Protection |  |  | overload protection, overheat protection, short circuit protection, fault pre-judgment, etc
Inverter | Output voltage |  |  | 3300V | [5 empty] | 6600V | 10kV | 6600V |  | 10kV
Max output frequency
| Speed stable accuracy |  |  | OLVC: 0.01%, CLVC: 0.01% | [7 empty] | OLVC: 0.01%, CLVC: 0.01%
| Speed pulse |  |  | OLVC: 0.2%, CLVC: 0.1% | [7 empty] | OLVC: 0.4%, CLVC: 0.2%
| Start torque |  |  | OLVC: 150%, CLVC: 200% | [7 empty] | OLVC: 130%, CLVC: 150%
| Torque control |  |  | V/F: Yes, OLVC: Yes, CLVC: Yes | [7 empty] | V/F: Yes, OLVC: Yes, CLVC: Yes
| Torque accuracy |  |  | OLVC: 5%, CLVC: 2% | [7 empty] | OLVC: 5%, CLVC: 2%
| Torque response time |  |  | OLVC: 5ms, CLVC: 5ms | [7 empty] | OLVC: 5ms, CLVC: 5ms
| Rotating response time |  |  | OLVC: 100ms, CLVC: 100ms | [7 empty] | OLVC: 150ms, CLVC: 150ms
| Dynamic drop equivalent |  |  | OLVC: 0.5%*s, CLVC: 0.25%*s | [7 empty] | OLVC: 1%*s, CLVC: 0.5%*s
| Overload |  |  | 110%@rated current, 120%@rated current 60s
Environment | Temperature |  |  | inlet temperature ≤40
| Altitude |  |  | ≤4000m (2000m~4000m de-rating)
Mechanical Data | IP protection |  |  | IP54
| Cooling |  |  | Water cooling
| Anti corrosion |  |  | C4-M
HD8000 Series Selection Table
Module |  | Grid Voltage | Motor Voltage |  | Power | RatedI |  | Max f | Size (W*D*H) (mm) |  |  |  | Note
HD8000-3306 |  | 3300V | 3300V |  | 6MVA | 1050A |  | 110Hz | 4600*1300*2200 |  |  |  | Contains water cool cabinet
HD8000-3308 |  |  |  |  | 8MVA | 1400A
HD8000-3310 |  |  |  |  | 10MVA | 1750A
HD8000-3312 |  |  |  |  | 12MVA | 2100A
HD8000-2624 |  | 1900V | 6600V |  | 24MVA | 2100A |  |  | 7800*1300*2200
HD8000-AA30 |  | 10kV | 10kV |  | 30MVA | 1750A |  |  | 10600*1300*2200
HD8000-6640 |  | 6600V | 6600V |  | 40MVA | 3500A |  |  | 15600*1300*2200
HD8000-AA60 |  | 10kV | 10kV |  | 60MVA | 3500A |  |  | 21200*1600*2200